Material Specification

Customer:  IEWC

TOL Part Number:		XHHW/SIS-F-10-2005

Spec Revision Level:		A2

Customer Part Number:	SIS10T105-X

Description:	10 AWG (5.26mm2) XHHW-2 & SIS (VW-1) Dual Rated, XLPE INSULATED 90 DegC 600V, 105 Strands Tinned Copper

Conductor (Stranding):	105 X 30 AWG Tinned Copper, UL

Conductor OD (Nom)		0.117 inches

Max. Lay Length:		2.0 inch Lay

Min Avg Wall Thickness:	0.030 inches

Min. O.D: 			0.178 inches

Nom. O. D:			0.181 inches

Max Runout:			0.008 inches

Strip Force:			1” Strippable

## Circular Mils (CMA):	10069 (Min)

## Surface Print:   	10 AWG (5.26mm2) (UL) XHHW-2 OR SIS VW-1 600V E7088 CSA c(UL) R90 600V FT1 FT2 LL25850

## This product is RoHS Compliant.

# Specification Reference Data

## SAE:	N/A			       Ford: N/A 		Chrysler: N/A

Packard: N/A		Other:	UL STD 44 / CSA 22.2#127-2009

Therm-O-Link, Inc. certifies that the above specifications are met or exceeded in the production of this product.

Verified By:			Mir Hussain (Corporate Product Engineering Manager)

Date:	2-25-2020