Material Specification

Customer :  IEWC

TOL Part Number:		XHHW/SIS-F-14-2005

Spec Revision Level:		A1

Description:	14 AWG (2.08mm2) XHHW-2 &  SIS (VW-1) Dual Rated, XLPE INSULATED 90 Deg C  600V, c(UL), 41 STRANDS TINNED

AWG:				14 Gauge

Conductor (Stranding):	41 X 30 AWG Tinned Copper, UL

Conductor OD (Nom)		0.069 inches

Max. Lay Length:		1.5 inch Lay

Min Avg Wall Thickness:	0.030 inches

Min. O.D: 			0.129 inches

Nom. O.D:			0.132 inches

Strip Force:			1” Strippable

## Circular Mils (CMA):	3987 (Min)

## Surface Print:   	14 AWG (2.08mm2) (UL) XHHW-2 OR SIS VW-1 600V E7088 CSA c(UL) R90 600V FT1 FT2 LL25850

This product is RoHS Compliant.

# Specification Reference Data

## SAE:	N/A			       Ford: N/A 		Chrysler: N/A

Packard: N/A		Other:	UL STD 44 / CSA 22.2#127-2009

Therm-O-Link, Inc. certifies that the above specifications are met or exceeded in the production of this product.

Verified By:			Mir Hussain (Corporate Product Engineering Manager)

Date:	2-25-2020